IEEE39Data.sav FVSI:

SIEMENS POWER TECHNOLOGIES INTERNATIONAL

50 BUS POWER SYSTEM SIMULATOR--PSS(R)E Xplore-36.6.0--Python 3.14

INITIATED ON THU, SEP 24 2026  16:32

From bus 2 to 3

Base FVSI       = 0.2479

V_send (pu)     = 1.0170

V_recv (pu)     = 0.9493

P_flow (MW)     = 169.6959

Q_recv (MVAR)   = 421.3066

Q_max (MVAR)    = 421.3066 (Actual network limit)

Q_margin (MVAR) = 0.0000 (Actual margin)

P_loss (MW)     = 2.8232

Q_loss (MVAR)   = 7.9026

From bus 19 to 16

Base FVSI       = 0.2015

V_send (pu)     = 1.0239

V_recv (pu)     = 0.9684

P_flow (MW)     = 212.4595

Q_recv (MVAR)   = 268.9943

Q_max (MVAR)    = 270.0533 (Actual network limit)

Q_margin (MVAR) = 1.0590 (Actual margin)

P_loss (MW)     = 1.8773

Q_loss (MVAR)   = -7.3113

From bus 29 to 26

Base FVSI       = 0.1841

V_send (pu)     = 1.0320

V_recv (pu)     = 1.0074

P_flow (MW)     = 113.7215

Q_recv (MVAR)   = 77.8020

Q_max (MVAR)    = 78.7447 (Actual network limit)

Q_margin (MVAR) = 0.9427 (Actual margin)

P_loss (MW)     = 0.7631

Q_loss (MVAR)   = -98.6480

From bus 22 to 21

Base FVSI       = 0.1297

V_send (pu)     = 1.0236

V_recv (pu)     = 0.9832

P_flow (MW)     = 566.5053

Q_recv (MVAR)   = 241.9220

Q_max (MVAR)    = 243.4961 (Actual network limit)

Q_margin (MVAR) = 1.5741 (Actual margin)

P_loss (MW)     = 3.0917

Q_loss (MVAR)   = 28.2674

From bus 28 to 26

Base FVSI       = 0.1283

V_send (pu)     = 1.0242

V_recv (pu)     = 1.0074

P_flow (MW)     = 47.7058

Q_recv (MVAR)   = 70.4187

Q_max (MVAR)    = 71.3710 (Actual network limit)

Q_margin (MVAR) = 0.9522 (Actual margin)

P_loss (MW)     = 0.1367

Q_loss (MVAR)   = -79.0027

From bus 23 to 24

Base FVSI       = 0.1147

V_send (pu)     = 1.0171

V_recv (pu)     = 0.9808

P_flow (MW)     = 304.6090

Q_recv (MVAR)   = 84.4072

Q_max (MVAR)    = 85.1640 (Actual network limit)

Q_margin (MVAR) = 0.7568 (Actual margin)

P_loss (MW)     = 2.1945

Q_loss (MVAR)   = -1.1226

From bus 26 to 27

Base FVSI       = 0.1023

V_send (pu)     = 1.0074

V_recv (pu)     = 0.9796

P_flow (MW)     = 200.6377

Q_recv (MVAR)   = 175.0261

Q_max (MVAR)    = 176.3854 (Actual network limit)

Q_margin (MVAR) = 1.3593 (Actual margin)

P_loss (MW)     = 0.9717

Q_loss (MVAR)   = -13.4530

From bus 14 to 4

Base FVSI       = 0.0731

V_send (pu)     = 0.8726

V_recv (pu)     = 0.8547

P_flow (MW)     = 206.3226

Q_recv (MVAR)   = 107.4686

Q_max (MVAR)    = 107.4686 (Actual network limit)

Q_margin (MVAR) = 0.0000 (Actual margin)

P_loss (MW)     = 0.5811

Q_loss (MVAR)   = -0.9390

From bus 21 to 16

Base FVSI       = 0.0584

V_send (pu)     = 0.9832

V_recv (pu)     = 0.9684

P_flow (MW)     = 196.1754

Q_recv (MVAR)   = 104.2502

Q_max (MVAR)    = 104.9863 (Actual network limit)

Q_margin (MVAR) = 0.7362 (Actual margin)

P_loss (MW)     = 0.4010

Q_loss (MVAR)   = -17.4976

From bus 1 to 39

Base FVSI       = 0.0553

V_send (pu)     = 1.0358

V_recv (pu)     = 1.0300

P_flow (MW)     = 87.1347

Q_recv (MVAR)   = 59.2110

Q_max (MVAR)    = 59.2106 (Actual network limit)

Q_margin (MVAR) = -0.0003 (Actual margin)

P_loss (MW)     = 0.0750

Q_loss (MVAR)   = -78.1396

From bus 25 to 26

Base FVSI       = 0.0455

V_send (pu)     = 1.0205

V_recv (pu)     = 1.0074

P_flow (MW)     = 228.5014

Q_recv (MVAR)   = 36.2905

Q_max (MVAR)    = 38.4292 (Actual network limit)

Q_margin (MVAR) = 2.1387 (Actual margin)

P_loss (MW)     = 1.6263

Q_loss (MVAR)   = -36.3282

From bus 5 to 8

Base FVSI       = 0.0290

V_send (pu)     = 0.8352

V_recv (pu)     = 0.8207

P_flow (MW)     = 570.8273

Q_recv (MVAR)   = 44.8542

Q_max (MVAR)    = 44.8542 (Actual network limit)

Q_margin (MVAR) = 0.0000 (Actual margin)

P_loss (MW)     = 3.8373

Q_loss (MVAR)   = 43.6034

From bus 22 to 23

Base FVSI       = 0.0269

V_send (pu)     = 1.0236

V_recv (pu)     = 1.0171

P_flow (MW)     = 80.4030

Q_recv (MVAR)   = 73.1640

Q_max (MVAR)    = 77.3342 (Actual network limit)

Q_margin (MVAR) = 4.1702 (Actual margin)

P_loss (MW)     = 0.0609

Q_loss (MVAR)   = -18.2435

From bus 6 to 7

Base FVSI       = 0.0258

V_send (pu)     = 0.8364

V_recv (pu)     = 0.8193

P_flow (MW)     = 876.6985

Q_recv (MVAR)   = 48.7962

Q_max (MVAR)    = 48.7962 (Actual network limit)

Q_margin (MVAR) = 0.0000 (Actual margin)

P_loss (MW)     = 6.7822

Q_loss (MVAR)   = 96.2464

From bus 25 to 2

Base FVSI       = 0.0236

V_send (pu)     = 1.0205

V_recv (pu)     = 1.0170

P_flow (MW)     = 7.1822

Q_recv (MVAR)   = 43.0161

Q_max (MVAR)    = 44.8189 (Actual network limit)

Q_margin (MVAR) = 1.8028 (Actual margin)

P_loss (MW)     = 0.0886

Q_loss (MVAR)   = -15.0434

From bus 10 to 13

Base FVSI       = 0.0226

V_send (pu)     = 0.8894

V_recv (pu)     = 0.8794

P_flow (MW)     = 898.9009

Q_recv (MVAR)   = 102.8855

Q_max (MVAR)    = 102.8855 (Actual network limit)

Q_margin (MVAR) = 0.0000 (Actual margin)

P_loss (MW)     = 4.1921

Q_loss (MVAR)   = 39.3627

From bus 29 to 28

Base FVSI       = 0.0164

V_send (pu)     = 1.0320

V_recv (pu)     = 1.0242

P_flow (MW)     = 325.9643

Q_recv (MVAR)   = 28.6567

Q_max (MVAR)    = 35.1525 (Actual network limit)

Q_margin (MVAR) = 6.4958 (Actual margin)

P_loss (MW)     = 1.4214

Q_loss (MVAR)   = -10.9891

From bus 16 to 17

Base FVSI       = 0.0043

V_send (pu)     = 0.9684

V_recv (pu)     = 0.9669

P_flow (MW)     = 127.3318

Q_recv (MVAR)   = 11.2810

Q_max (MVAR)    = 12.9747 (Actual network limit)

Q_margin (MVAR) = 1.6937 (Actual margin)

P_loss (MW)     = 0.1213

Q_loss (MVAR)   = -11.0236

RESULT ANALYSIS

Most critical corridor: Bus 2 to 3 (FVSI = 0.2479)

This line can absorb only 0.00 MVAR more before experiencing collapse.

Corridor is stressed.

IEEE14Data.sav FVSI:

SIEMENS POWER TECHNOLOGIES INTERNATIONAL

50 BUS POWER SYSTEM SIMULATOR--PSS(R)E Xplore-36.6.0--Python 3.14

INITIATED ON THU, SEP 24 2026  16:33

From bus 1 to 5

Base FVSI       = 0.3727

V_send (pu)     = 1.0600

V_recv (pu)     = 0.8065

P_flow (MW)     = 141.8640

Q_recv (MVAR)   = 44.3343

Q_max (MVAR)    = 44.3343 (Actual network limit)

Q_margin (MVAR) = 0.0000 (Actual margin)

P_loss (MW)     = 14.9050

Q_loss (MVAR)   = 57.1646

From bus 1 to 2

Base FVSI       = 0.2492

V_send (pu)     = 1.0600

V_recv (pu)     = 0.9141

P_flow (MW)     = 325.2063

Q_recv (MVAR)   = 106.8517

Q_max (MVAR)    = 110.5819 (Actual network limit)

Q_margin (MVAR) = 3.7302 (Actual margin)

P_loss (MW)     = 23.6330

Q_loss (MVAR)   = 66.9827

From bus 7 to 9

Base FVSI       = 0.2229

V_send (pu)     = 0.7529

V_recv (pu)     = 0.7043

P_flow (MW)     = 48.1404

Q_recv (MVAR)   = 28.7108

Q_max (MVAR)    = 28.7108 (Actual network limit)

Q_margin (MVAR) = 0.0000 (Actual margin)

P_loss (MW)     = 0.0000

Q_loss (MVAR)   = 6.9674

From bus 2 to 5

Base FVSI       = 0.2214

V_send (pu)     = 0.9141

V_recv (pu)     = 0.8065

P_flow (MW)     = 73.4357

Q_recv (MVAR)   = 24.0232

Q_max (MVAR)    = 24.0232 (Actual network limit)

Q_margin (MVAR) = 0.0000 (Actual margin)

P_loss (MW)     = 4.6066

Q_loss (MVAR)   = 11.4940

From bus 2 to 4

Base FVSI       = 0.1829

V_send (pu)     = 0.9141

V_recv (pu)     = 0.7833

P_flow (MW)     = 100.5268

Q_recv (MVAR)   = 19.5490

Q_max (MVAR)    = 19.5490 (Actual network limit)

Q_margin (MVAR) = 0.0000 (Actual margin)

P_loss (MW)     = 8.3677

Q_loss (MVAR)   = 22.9261

From bus 6 to 13

Base FVSI       = 0.1671

V_send (pu)     = 0.7498

V_recv (pu)     = 0.6936

P_flow (MW)     = 30.9712

Q_recv (MVAR)   = 14.3285

Q_max (MVAR)    = 14.3285 (Actual network limit)

Q_margin (MVAR) = 0.0000 (Actual margin)

P_loss (MW)     = 1.4784

Q_loss (MVAR)   = 2.9114

From bus 9 to 14

Base FVSI       = 0.1555

V_send (pu)     = 0.7043

V_recv (pu)     = 0.6474

P_flow (MW)     = 16.3738

Q_recv (MVAR)   = 5.8398

Q_max (MVAR)    = 5.8398 (Actual network limit)

Q_margin (MVAR) = 0.0000 (Actual margin)

P_loss (MW)     = 0.8356

Q_loss (MVAR)   = 1.7775

From bus 6 to 11

Base FVSI       = 0.1402

V_send (pu)     = 0.7498

V_recv (pu)     = 0.7107

P_flow (MW)     = 12.4951

Q_recv (MVAR)   = 8.0669

Q_max (MVAR)    = 8.0669 (Actual network limit)

Q_margin (MVAR) = 0.0000 (Actual margin)

P_loss (MW)     = 0.3976

Q_loss (MVAR)   = 0.8326

From bus 13 to 14

Base FVSI       = 0.1388

V_send (pu)     = 0.6936

V_recv (pu)     = 0.6474

P_flow (MW)     = 9.6106

Q_recv (MVAR)   = 3.8652

Q_max (MVAR)    = 3.8652 (Actual network limit)

Q_margin (MVAR) = 0.0000 (Actual margin)

P_loss (MW)     = 0.4064

Q_loss (MVAR)   = 0.8275

From bus 6 to 12

Base FVSI       = 0.1117

V_send (pu)     = 0.7498

V_recv (pu)     = 0.7079

P_flow (MW)     = 13.6802

Q_recv (MVAR)   = 4.9843

Q_max (MVAR)    = 4.9843 (Actual network limit)

Q_margin (MVAR) = 0.0000 (Actual margin)

P_loss (MW)     = 0.4879

Q_loss (MVAR)   = 1.0154

From bus 2 to 3

Base FVSI       = 0.0895

V_send (pu)     = 0.9141

V_recv (pu)     = 0.7697

P_flow (MW)     = 131.0461

Q_recv (MVAR)   = 8.9436

Q_max (MVAR)    = 8.9436 (Actual network limit)

Q_margin (MVAR) = 0.0000 (Actual margin)

P_loss (MW)     = 11.4006

Q_loss (MVAR)   = 44.9034

From bus 11 to 10

Base FVSI       = 0.0773

V_send (pu)     = 0.7107

V_recv (pu)     = 0.6914

P_flow (MW)     = 6.1045

Q_recv (MVAR)   = 4.2979

Q_max (MVAR)    = 4.2979 (Actual network limit)

Q_margin (MVAR) = 0.0000 (Actual margin)

P_loss (MW)     = 0.0957

Q_loss (MVAR)   = 0.2239

From bus 12 to 13

Base FVSI       = 0.0633

V_send (pu)     = 0.7079

V_recv (pu)     = 0.6936

P_flow (MW)     = 2.9142

Q_recv (MVAR)   = 1.7858

Q_max (MVAR)    = 1.7858 (Actual network limit)

Q_margin (MVAR) = 0.0000 (Actual margin)

P_loss (MW)     = 0.0523

Q_loss (MVAR)   = 0.0473

From bus 9 to 10

Base FVSI       = 0.0554

V_send (pu)     = 0.7043

V_recv (pu)     = 0.6914

P_flow (MW)     = 9.1442

Q_recv (MVAR)   = 7.1219

Q_max (MVAR)    = 7.1219 (Actual network limit)

Q_margin (MVAR) = 0.0000 (Actual margin)

P_loss (MW)     = 0.0883

Q_loss (MVAR)   = 0.2346

From bus 5 to 4

Base FVSI       = 0.0185

V_send (pu)     = 0.8065

V_recv (pu)     = 0.7833

P_flow (MW)     = 104.5745

Q_recv (MVAR)   = 6.5041

Q_max (MVAR)    = 6.5041 (Actual network limit)

Q_margin (MVAR) = 0.0000 (Actual margin)

P_loss (MW)     = 2.3885

Q_loss (MVAR)   = 7.5340

RESULT ANALYSIS

Most critical corridor: Bus 1 to 5 (FVSI = 0.3727)

This line can absorb only 0.00 MVAR more before experiencing collapse.

Corridor is stressed.

IEEE39Data_Tap Change FVSI:

SIEMENS POWER TECHNOLOGIES INTERNATIONAL

50 BUS POWER SYSTEM SIMULATOR--PSS(R)E Xplore-36.6.0--Python 3.14

INITIATED ON THU, SEP 24 2026  16:34

From bus 19 to 16

Base FVSI       = 0.2104

V_send (pu)     = 1.0807

V_recv (pu)     = 1.0200

P_flow (MW)     = 212.1752

Q_recv (MVAR)   = 313.0138

Q_max (MVAR)    = 731.4576 (Actual network limit)

Q_margin (MVAR) = 418.4439 (Actual margin)

P_loss (MW)     = 2.0507

Q_loss (MVAR)   = -8.5753

From bus 2 to 3

Base FVSI       = 0.1819

V_send (pu)     = 1.0602

V_recv (pu)     = 1.0096

P_flow (MW)     = 163.0945

Q_recv (MVAR)   = 336.0421

Q_max (MVAR)    = 848.6501 (Actual network limit)

Q_margin (MVAR) = 512.6080 (Actual margin)

P_loss (MW)     = 1.6624

Q_loss (MVAR)   = -8.2519

From bus 29 to 26

Base FVSI       = 0.1154

V_send (pu)     = 1.0466

V_recv (pu)     = 1.0414

P_flow (MW)     = 114.3367

Q_recv (MVAR)   = 50.1287

Q_max (MVAR)    = 251.1486 (Actual network limit)

Q_margin (MVAR) = 201.0199 (Actual margin)

P_loss (MW)     = 0.6887

Q_loss (MVAR)   = -104.6038

From bus 1 to 39

Base FVSI       = 0.1151

V_send (pu)     = 1.0523

V_recv (pu)     = 1.0300

P_flow (MW)     = 90.4181

Q_recv (MVAR)   = 127.2105

Q_max (MVAR)    = 318.3216 (Actual network limit)

Q_margin (MVAR) = 191.1111 (Actual margin)

P_loss (MW)     = 0.1488

Q_loss (MVAR)   = -77.5880

From bus 22 to 21

Base FVSI       = 0.0789

V_send (pu)     = 1.0495

V_recv (pu)     = 1.0229

P_flow (MW)     = 566.6010

Q_recv (MVAR)   = 154.6799

Q_max (MVAR)    = 753.0618 (Actual network limit)

Q_margin (MVAR) = 598.3818 (Actual margin)

P_loss (MW)     = 2.6071

Q_loss (MVAR)   = 18.0802

From bus 28 to 26

Base FVSI       = 0.0745

V_send (pu)     = 1.0437

V_recv (pu)     = 1.0414

P_flow (MW)     = 47.3770

Q_recv (MVAR)   = 42.4560

Q_max (MVAR)    = 246.0643 (Actual network limit)

Q_margin (MVAR) = 203.6083 (Actual margin)

P_loss (MW)     = 0.0890

Q_loss (MVAR)   = -83.8220

From bus 2 to 1

Base FVSI       = 0.0731

V_send (pu)     = 1.0602

V_recv (pu)     = 1.0523

P_flow (MW)     = 90.4181

Q_recv (MVAR)   = 49.6224

Q_max (MVAR)    = 492.1628 (Actual network limit)

Q_margin (MVAR) = 442.5403 (Actual margin)

P_loss (MW)     = 0.2622

Q_loss (MVAR)   = -74.8715

From bus 26 to 27

Base FVSI       = 0.0680

V_send (pu)     = 1.0414

V_recv (pu)     = 1.0222

P_flow (MW)     = 204.1894

Q_recv (MVAR)   = 124.2738

Q_max (MVAR)    = 648.1569 (Actual network limit)

Q_margin (MVAR) = 523.8831 (Actual margin)

P_loss (MW)     = 0.7220

Q_loss (MVAR)   = -17.9306

From bus 23 to 24

Base FVSI       = 0.0501

V_send (pu)     = 1.0476

V_recv (pu)     = 1.0292

P_flow (MW)     = 305.0320

Q_recv (MVAR)   = 39.1488

Q_max (MVAR)    = 374.8246 (Actual network limit)

Q_margin (MVAR) = 335.6758 (Actual margin)

P_loss (MW)     = 1.9165

Q_loss (MVAR)   = -8.4388

From bus 5 to 8

Base FVSI       = 0.0456

V_send (pu)     = 0.9415

V_recv (pu)     = 0.9242

P_flow (MW)     = 563.6408

Q_recv (MVAR)   = 89.8111

Q_max (MVAR)    = 239.1734 (Actual network limit)

Q_margin (MVAR) = 149.3623 (Actual margin)

P_loss (MW)     = 3.0093

Q_loss (MVAR)   = 29.2858

From bus 25 to 26

Base FVSI       = 0.0431

V_send (pu)     = 1.0537

V_recv (pu)     = 1.0414

P_flow (MW)     = 231.7054

Q_recv (MVAR)   = 36.6966

Q_max (MVAR)    = 512.4259 (Actual network limit)

Q_margin (MVAR) = 475.7293 (Actual margin)

P_loss (MW)     = 1.5650

Q_loss (MVAR)   = -40.5002

From bus 6 to 7

Base FVSI       = 0.0411

V_send (pu)     = 0.9445

V_recv (pu)     = 0.9256

P_flow (MW)     = 873.8274

Q_recv (MVAR)   = 99.1720

Q_max (MVAR)    = 306.1391 (Actual network limit)

Q_margin (MVAR) = 206.9671 (Actual margin)

P_loss (MW)     = 5.3447

Q_loss (MVAR)   = 72.0696

From bus 14 to 4

Base FVSI       = 0.0206

V_send (pu)     = 0.9499

V_recv (pu)     = 0.9439

P_flow (MW)     = 193.6684

Q_recv (MVAR)   = 35.9080

Q_max (MVAR)    = 251.9924 (Actual network limit)

Q_margin (MVAR) = 216.0844 (Actual margin)

P_loss (MW)     = 0.3448

Q_loss (MVAR)   = -6.8323

From bus 21 to 16

Base FVSI       = 0.0109

V_send (pu)     = 1.0229

V_recv (pu)     = 1.0200

P_flow (MW)     = 196.3750

Q_recv (MVAR)   = 21.0838

Q_max (MVAR)    = 353.2446 (Actual network limit)

Q_margin (MVAR) = 332.1608 (Actual margin)

P_loss (MW)     = 0.2970

Q_loss (MVAR)   = -21.5733

From bus 22 to 23

Base FVSI       = 0.0089

V_send (pu)     = 1.0495

V_recv (pu)     = 1.0476

P_flow (MW)     = 80.7919

Q_recv (MVAR)   = 25.5279

Q_max (MVAR)    = 654.6799 (Actual network limit)

Q_margin (MVAR) = 629.1520 (Actual margin)

P_loss (MW)     = 0.0370

Q_loss (MVAR)   = -19.7032

From bus 16 to 17

Base FVSI       = 0.0057

V_send (pu)     = 1.0200

V_recv (pu)     = 1.0183

P_flow (MW)     = 122.7154

Q_recv (MVAR)   = 16.5536

Q_max (MVAR)    = 747.5315 (Actual network limit)

Q_margin (MVAR) = 730.9779 (Actual margin)

P_loss (MW)     = 0.1021

Q_loss (MVAR)   = -12.6401

From bus 10 to 13

Base FVSI       = 0.0052

V_send (pu)     = 0.9560

V_recv (pu)     = 0.9504

P_flow (MW)     = 875.8555

Q_recv (MVAR)   = 27.1902

Q_max (MVAR)    = 395.1335 (Actual network limit)

Q_margin (MVAR) = 367.9433 (Actual margin)

P_loss (MW)     = 3.3734

Q_loss (MVAR)   = 29.6400

RESULT ANALYSIS

Most critical corridor: Bus 19 to 16 (FVSI = 0.2104)

This line can absorb only 418.44 MVAR more before experiencing collapse.

Corridor is stressed.

# IEEE14Data_Tap Change FVSI:

50 BUS POWER SYSTEM SIMULATOR--PSS(R)E Xplore-36.6.0--Python 3.14

INITIATED ON THU, SEP 24 2026  16:35

From bus 1 to 5

Base FVSI       = 0.2896

V_send (pu)     = 1.0600

V_recv (pu)     = 0.8442

P_flow (MW)     = 140.3539

Q_recv (MVAR)   = 34.4491

Q_max (MVAR)    = 53.6028 (Actual network limit)

Q_margin (MVAR) = 19.1537 (Actual margin)

P_loss (MW)     = 13.0900

Q_loss (MVAR)   = 49.5193

From bus 1 to 2

Base FVSI       = 0.1904

V_send (pu)     = 1.0600

V_recv (pu)     = 0.9341

P_flow (MW)     = 318.2045

Q_recv (MVAR)   = 81.6427

Q_max (MVAR)    = 155.7280 (Actual network limit)

Q_margin (MVAR) = 74.0853 (Actual margin)

P_loss (MW)     = 21.0165

Q_loss (MVAR)   = 58.8969

From bus 7 to 9

Base FVSI       = 0.1841

V_send (pu)     = 0.8930

V_recv (pu)     = 0.8474

P_flow (MW)     = 48.8953

Q_recv (MVAR)   = 33.3621

Q_max (MVAR)    = 39.6000 (Actual network limit)

Q_margin (MVAR) = 6.2378 (Actual margin)

P_loss (MW)     = 0.0000

Q_loss (MVAR)   = 5.3675

From bus 2 to 5

Base FVSI       = 0.1594

V_send (pu)     = 0.9341

V_recv (pu)     = 0.8442

P_flow (MW)     = 72.4275

Q_recv (MVAR)   = 18.0634

Q_max (MVAR)    = 30.2525 (Actual network limit)

Q_margin (MVAR) = 12.1891 (Actual margin)

P_loss (MW)     = 3.9714

Q_loss (MVAR)   = 9.3832

From bus 2 to 4

Base FVSI       = 0.1190

V_send (pu)     = 0.9341

V_recv (pu)     = 0.8244

P_flow (MW)     = 99.0454

Q_recv (MVAR)   = 13.2809

Q_max (MVAR)    = 24.5809 (Actual network limit)

Q_margin (MVAR) = 11.3000 (Actual margin)

P_loss (MW)     = 7.3189

Q_loss (MVAR)   = 19.5685

From bus 6 to 13

Base FVSI       = 0.1172

V_send (pu)     = 0.8837

V_recv (pu)     = 0.8378

P_flow (MW)     = 30.7756

Q_recv (MVAR)   = 13.9573

Q_max (MVAR)    = 19.5489 (Actual network limit)

Q_margin (MVAR) = 5.5916 (Actual margin)

P_loss (MW)     = 1.0182

Q_loss (MVAR)   = 2.0051

From bus 9 to 14

Base FVSI       = 0.1142

V_send (pu)     = 0.8474

V_recv (pu)     = 0.8008

P_flow (MW)     = 16.0525

Q_recv (MVAR)   = 6.2124

Q_max (MVAR)    = 11.5949 (Actual network limit)

Q_margin (MVAR) = 5.3825 (Actual margin)

P_loss (MW)     = 0.5527

Q_loss (MVAR)   = 1.1757

From bus 6 to 11

Base FVSI       = 0.0942

V_send (pu)     = 0.8837

V_recv (pu)     = 0.8518

P_flow (MW)     = 12.8557

Q_recv (MVAR)   = 7.5313

Q_max (MVAR)    = 14.0974 (Actual network limit)

Q_margin (MVAR) = 6.5661 (Actual margin)

P_loss (MW)     = 0.2812

Q_loss (MVAR)   = 0.5889

From bus 13 to 14

Base FVSI       = 0.0895

V_send (pu)     = 0.8378

V_recv (pu)     = 0.8008

P_flow (MW)     = 9.8877

Q_recv (MVAR)   = 3.6351

Q_max (MVAR)    = 7.2432 (Actual network limit)

Q_margin (MVAR) = 3.6082 (Actual margin)

P_loss (MW)     = 0.2812

Q_loss (MVAR)   = 0.5726

From bus 6 to 12

Base FVSI       = 0.0783

V_send (pu)     = 0.8837

V_recv (pu)     = 0.8494

P_flow (MW)     = 13.5274

Q_recv (MVAR)   = 4.8560

Q_max (MVAR)    = 11.8635 (Actual network limit)

Q_margin (MVAR) = 7.0075 (Actual margin)

P_loss (MW)     = 0.3366

Q_loss (MVAR)   = 0.7006

From bus 2 to 3

Base FVSI       = 0.0627

V_send (pu)     = 0.9341

V_recv (pu)     = 0.8064

P_flow (MW)     = 129.1511

Q_recv (MVAR)   = 6.5400

Q_max (MVAR)    = 18.7004 (Actual network limit)

Q_margin (MVAR) = 12.1604 (Actual margin)

P_loss (MW)     = 10.2371

Q_loss (MVAR)   = 39.7943

From bus 11 to 10

Base FVSI       = 0.0479

V_send (pu)     = 0.8518

V_recv (pu)     = 0.8365

P_flow (MW)     = 6.6086

Q_recv (MVAR)   = 3.8261

Q_max (MVAR)    = 7.3802 (Actual network limit)

Q_margin (MVAR) = 3.5541 (Actual margin)

P_loss (MW)     = 0.0684

Q_loss (MVAR)   = 0.1601

From bus 12 to 13

Base FVSI       = 0.0412

V_send (pu)     = 0.8494

V_recv (pu)     = 0.8378

P_flow (MW)     = 2.9124

Q_recv (MVAR)   = 1.6733

Q_max (MVAR)    = 3.0925 (Actual network limit)

Q_margin (MVAR) = 1.4192 (Actual margin)

P_loss (MW)     = 0.0349

Q_loss (MVAR)   = 0.0316

From bus 9 to 10

Base FVSI       = 0.0408

V_send (pu)     = 0.8474

V_recv (pu)     = 0.8365

P_flow (MW)     = 8.6157

Q_recv (MVAR)   = 7.5969

Q_max (MVAR)    = 16.0222 (Actual network limit)

Q_margin (MVAR) = 8.4253 (Actual margin)

P_loss (MW)     = 0.0595

Q_loss (MVAR)   = 0.1581

From bus 5 to 4

Base FVSI       = 0.0056

V_send (pu)     = 0.8442

V_recv (pu)     = 0.8244

P_flow (MW)     = 104.7286

Q_recv (MVAR)   = 2.1522

Q_max (MVAR)    = 17.3217 (Actual network limit)

Q_margin (MVAR) = 15.1695 (Actual margin)

P_loss (MW)     = 2.1551

Q_loss (MVAR)   = 6.7979

RESULT ANALYSIS

Most critical corridor: Bus 1 to 5 (FVSI = 0.2896)

This line can absorb only 19.15 MVAR more before experiencing collapse.

Corridor is stressed.

# IEEE39Data 12 Capacitor & 100MVAr FVSI:

SIEMENS POWER TECHNOLOGIES INTERNATIONAL

50 BUS POWER SYSTEM SIMULATOR--PSS(R)E Xplore-36.6.0--Python 3.14

INITIATED ON THU, SEP 24 2026  16:36

From bus 1 to 39

Base FVSI       = 0.1005

V_send (pu)     = 1.0482

V_recv (pu)     = 1.0300

P_flow (MW)     = 91.6162

Q_recv (MVAR)   = 110.2575

Q_max (MVAR)    = 315.8239 (Actual network limit)

Q_margin (MVAR) = 205.5665 (Actual margin)

P_loss (MW)     = 0.1257

Q_loss (MVAR)   = -77.8441

From bus 29 to 26

Base FVSI       = 0.0979

V_send (pu)     = 1.0454

V_recv (pu)     = 1.0451

P_flow (MW)     = 114.4564

Q_recv (MVAR)   = 42.4393

Q_max (MVAR)    = 243.7768 (Actual network limit)

Q_margin (MVAR) = 201.3375 (Actual margin)

P_loss (MW)     = 0.6935

Q_loss (MVAR)   = -104.8288

From bus 2 to 3

Base FVSI       = 0.0882

V_send (pu)     = 1.0496

V_recv (pu)     = 1.0256

P_flow (MW)     = 168.4293

Q_recv (MVAR)   = 159.7582

Q_max (MVAR)    = 839.9465 (Actual network limit)

Q_margin (MVAR) = 680.1883 (Actual margin)

P_loss (MW)     = 0.6123

Q_loss (MVAR)   = -20.5824

From bus 28 to 26

Base FVSI       = 0.0609

V_send (pu)     = 1.0437

V_recv (pu)     = 1.0451

P_flow (MW)     = 47.2625

Q_recv (MVAR)   = 34.7051

Q_max (MVAR)    = 238.7667 (Actual network limit)

Q_margin (MVAR) = 204.0616 (Actual margin)

P_loss (MW)     = 0.0904

Q_loss (MVAR)   = -84.1112

From bus 14 to 4

Base FVSI       = 0.0585

V_send (pu)     = 1.0098

V_recv (pu)     = 0.9939

P_flow (MW)     = 196.5054

Q_recv (MVAR)   = 115.2339

Q_max (MVAR)    = 355.3736 (Actual network limit)

Q_margin (MVAR) = 240.1397 (Actual margin)

P_loss (MW)     = 0.4079

Q_loss (MVAR)   = -7.2938

From bus 19 to 16

Base FVSI       = 0.0505

V_send (pu)     = 1.0480

V_recv (pu)     = 1.0337

P_flow (MW)     = 214.4346

Q_recv (MVAR)   = 70.6763

Q_max (MVAR)    = 658.4739 (Actual network limit)

Q_margin (MVAR) = 587.7976 (Actual margin)

P_loss (MW)     = 0.7329

Q_loss (MVAR)   = -24.0021

From bus 2 to 1

Base FVSI       = 0.0487

V_send (pu)     = 1.0496

V_recv (pu)     = 1.0482

P_flow (MW)     = 91.6162

Q_recv (MVAR)   = 32.4133

Q_max (MVAR)    = 481.7004 (Actual network limit)

Q_margin (MVAR) = 449.2871 (Actual margin)

P_loss (MW)     = 0.2685

Q_loss (MVAR)   = -73.7150

From bus 22 to 21

Base FVSI       = 0.0450

V_send (pu)     = 1.0494

V_recv (pu)     = 1.0321

P_flow (MW)     = 567.8571

Q_recv (MVAR)   = 88.1520

Q_max (MVAR)    = 746.1347 (Actual network limit)

Q_margin (MVAR) = 657.9827 (Actual margin)

P_loss (MW)     = 2.4636

Q_loss (MVAR)   = 15.3303

From bus 26 to 27

Base FVSI       = 0.0428

V_send (pu)     = 1.0451

V_recv (pu)     = 1.0327

P_flow (MW)     = 198.0633

Q_recv (MVAR)   = 78.7716

Q_max (MVAR)    = 648.8904 (Actual network limit)

Q_margin (MVAR) = 570.1188 (Actual margin)

P_loss (MW)     = 0.5692

Q_loss (MVAR)   = -19.8863

From bus 9 to 39

Base FVSI       = 0.0314

V_send (pu)     = 1.0311

V_recv (pu)     = 1.0300

P_flow (MW)     = 400.5357

Q_recv (MVAR)   = 33.3531

Q_max (MVAR)    = 135.4985 (Actual network limit)

Q_margin (MVAR) = 102.1455 (Actual margin)

P_loss (MW)     = 1.5095

Q_loss (MVAR)   = -89.7079

From bus 22 to 23

Base FVSI       = 0.0247

V_send (pu)     = 1.0494

V_recv (pu)     = 1.0433

P_flow (MW)     = 79.6794

Q_recv (MVAR)   = 70.5195

Q_max (MVAR)    = 698.8633 (Actual network limit)

Q_margin (MVAR) = 628.3438 (Actual margin)

P_loss (MW)     = 0.0551

Q_loss (MVAR)   = -19.3286

From bus 5 to 8

Base FVSI       = 0.0162

V_send (pu)     = 0.9962

V_recv (pu)     = 0.9864

P_flow (MW)     = 561.5637

Q_recv (MVAR)   = 35.5928

Q_max (MVAR)    = 242.3533 (Actual network limit)

Q_margin (MVAR) = 206.7605 (Actual margin)

P_loss (MW)     = 2.5759

Q_loss (MVAR)   = 21.5587

From bus 17 to 27

Base FVSI       = 0.0150

V_send (pu)     = 1.0364

V_recv (pu)     = 1.0327

P_flow (MW)     = 182.2893

Q_recv (MVAR)   = 23.1005

Q_max (MVAR)    = 710.5322 (Actual network limit)

Q_margin (MVAR) = 687.4317 (Actual margin)

P_loss (MW)     = 0.4037

Q_loss (MVAR)   = -29.0508

From bus 25 to 26

Base FVSI       = 0.0056

V_send (pu)     = 1.0471

V_recv (pu)     = 1.0451

P_flow (MW)     = 225.4952

Q_recv (MVAR)   = 4.6789

Q_max (MVAR)    = 520.0330 (Actual network limit)

Q_margin (MVAR) = 515.3540 (Actual margin)

P_loss (MW)     = 1.4860

Q_loss (MVAR)   = -41.1432

RESULT ANALYSIS

Most critical corridor: Bus 1 to 39 (FVSI = 0.1005)

This line can absorb only 205.57 MVAR more before experiencing collapse.

System is highly secure.

# IEEE39Data 29(selected- total PQ available) Capacitor & 100MVAr FVSI:

SIEMENS POWER TECHNOLOGIES INTERNATIONAL

50 BUS POWER SYSTEM SIMULATOR--PSS(R)E Xplore-36.6.0--Python 3.14

INITIATED ON THU, SEP 24 2026  16:38

From bus 29 to 26

Base FVSI       = 0.1148

V_send (pu)     = 1.0492

V_recv (pu)     = 1.0443

P_flow (MW)     = 114.3597

Q_recv (MVAR)   = 50.1543

Q_max (MVAR)    = 255.8181 (Actual network limit)

Q_margin (MVAR) = 205.6638 (Actual margin)

P_loss (MW)     = 0.6854

Q_loss (MVAR)   = -105.2289

From bus 1 to 39

Base FVSI       = 0.1006

V_send (pu)     = 1.0483

V_recv (pu)     = 1.0300

P_flow (MW)     = 92.6724

Q_recv (MVAR)   = 110.3614

Q_max (MVAR)    = 313.0286 (Actual network limit)

Q_margin (MVAR) = 202.6672 (Actual margin)

P_loss (MW)     = 0.1277

Q_loss (MVAR)   = -77.7982

From bus 2 to 3

Base FVSI       = 0.0866

V_send (pu)     = 1.0497

V_recv (pu)     = 1.0263

P_flow (MW)     = 166.4663

Q_recv (MVAR)   = 156.8589

Q_max (MVAR)    = 801.3124 (Actual network limit)

Q_margin (MVAR) = 644.4535 (Actual margin)

P_loss (MW)     = 0.5931

Q_loss (MVAR)   = -20.8254

From bus 19 to 16

Base FVSI       = 0.0859

V_send (pu)     = 1.0486

V_recv (pu)     = 1.0247

P_flow (MW)     = 214.4433

Q_recv (MVAR)   = 120.3049

Q_max (MVAR)    = 647.1260 (Actual network limit)

Q_margin (MVAR) = 526.8211 (Actual margin)

P_loss (MW)     = 0.8667

Q_loss (MVAR)   = -22.1088

From bus 28 to 26

Base FVSI       = 0.0741

V_send (pu)     = 1.0464

V_recv (pu)     = 1.0443

P_flow (MW)     = 47.3937

Q_recv (MVAR)   = 42.4732

Q_max (MVAR)    = 250.8544 (Actual network limit)

Q_margin (MVAR) = 208.3812 (Actual margin)

P_loss (MW)     = 0.0886

Q_loss (MVAR)   = -84.2796

From bus 22 to 21

Base FVSI       = 0.0653

V_send (pu)     = 1.0468

V_recv (pu)     = 1.0240

P_flow (MW)     = 567.0909

Q_recv (MVAR)   = 127.3285

Q_max (MVAR)    = 751.9050 (Actual network limit)

Q_margin (MVAR) = 624.5766 (Actual margin)

P_loss (MW)     = 2.5527

Q_loss (MVAR)   = 17.1734

From bus 26 to 27

Base FVSI       = 0.0523

V_send (pu)     = 1.0443

V_recv (pu)     = 1.0293

P_flow (MW)     = 198.9779

Q_recv (MVAR)   = 96.0397

Q_max (MVAR)    = 652.2130 (Actual network limit)

Q_margin (MVAR) = 556.1733 (Actual margin)

P_loss (MW)     = 0.6117

Q_loss (MVAR)   = -19.3337

From bus 2 to 1

Base FVSI       = 0.0489

V_send (pu)     = 1.0497

V_recv (pu)     = 1.0483

P_flow (MW)     = 92.6724

Q_recv (MVAR)   = 32.5632

Q_max (MVAR)    = 481.7520 (Actual network limit)

Q_margin (MVAR) = 449.1888 (Actual margin)

P_loss (MW)     = 0.2746

Q_loss (MVAR)   = -73.6569

From bus 5 to 8

Base FVSI       = 0.0368

V_send (pu)     = 0.9859

V_recv (pu)     = 0.9709

P_flow (MW)     = 561.5365

Q_recv (MVAR)   = 79.3835

Q_max (MVAR)    = 253.2408 (Actual network limit)

Q_margin (MVAR) = 173.8573 (Actual margin)

P_loss (MW)     = 2.6950

Q_loss (MVAR)   = 23.6002

From bus 14 to 4

Base FVSI       = 0.0341

V_send (pu)     = 1.0005

V_recv (pu)     = 0.9909

P_flow (MW)     = 196.6267

Q_recv (MVAR)   = 65.8500

Q_max (MVAR)    = 303.2361 (Actual network limit)

Q_margin (MVAR) = 237.3861 (Actual margin)

P_loss (MW)     = 0.3434

Q_loss (MVAR)   = -8.1635

From bus 23 to 24

Base FVSI       = 0.0204

V_send (pu)     = 1.0429

V_recv (pu)     = 1.0325

P_flow (MW)     = 304.7234

Q_recv (MVAR)   = 15.7606

Q_max (MVAR)    = 376.8872 (Actual network limit)

Q_margin (MVAR) = 361.1266 (Actual margin)

P_loss (MW)     = 1.8927

Q_loss (MVAR)   = -8.7621

From bus 22 to 23

Base FVSI       = 0.0166

V_send (pu)     = 1.0468

V_recv (pu)     = 1.0429

P_flow (MW)     = 80.3564

Q_recv (MVAR)   = 47.1481

Q_max (MVAR)    = 671.1599 (Actual network limit)

Q_margin (MVAR) = 624.0118 (Actual margin)

P_loss (MW)     = 0.0432

Q_loss (MVAR)   = -19.4607

From bus 6 to 7

Base FVSI       = 0.0109

V_send (pu)     = 0.9844

V_recv (pu)     = 0.9735

P_flow (MW)     = 871.5514

Q_recv (MVAR)   = 28.5862

Q_max (MVAR)    = 283.8958 (Actual network limit)

Q_margin (MVAR) = 255.3095 (Actual margin)

P_loss (MW)     = 4.7605

Q_loss (MVAR)   = 62.1670

From bus 25 to 26

Base FVSI       = 0.0084

V_send (pu)     = 1.0470

V_recv (pu)     = 1.0443

P_flow (MW)     = 226.3862

Q_recv (MVAR)   = 7.0166

Q_max (MVAR)    = 516.7731 (Actual network limit)

Q_margin (MVAR) = 509.7565 (Actual margin)

P_loss (MW)     = 1.4970

Q_loss (MVAR)   = -40.9813

From bus 9 to 39

Base FVSI       = 0.0055

V_send (pu)     = 1.0244

V_recv (pu)     = 1.0300

P_flow (MW)     = 399.4965

Q_recv (MVAR)   = 5.7537

Q_max (MVAR)    = 105.2781 (Actual network limit)

Q_margin (MVAR) = 99.5244 (Actual margin)

P_loss (MW)     = 1.5245

Q_loss (MVAR)   = -88.5087

From bus 17 to 27

Base FVSI       = 0.0038

V_send (pu)     = 1.0302

V_recv (pu)     = 1.0293

P_flow (MW)     = 181.4171

Q_recv (MVAR)   = 5.8325

Q_max (MVAR)    = 687.5211 (Actual network limit)

Q_margin (MVAR) = 681.6886 (Actual margin)

P_loss (MW)     = 0.4036

Q_loss (MVAR)   = -28.7310

From bus 7 to 8

Base FVSI       = 0.0005

V_send (pu)     = 0.9735

V_recv (pu)     = 0.9709

P_flow (MW)     = 551.1360

Q_recv (MVAR)   = 2.6237

Q_max (MVAR)    = 137.3908 (Actual network limit)

Q_margin (MVAR) = 134.7671 (Actual margin)

P_loss (MW)     = 1.2830

Q_loss (MVAR)   = 7.3823

RESULT ANALYSIS

Most critical corridor: Bus 29 to 26 (FVSI = 0.1148)

This line can absorb only 205.66 MVAR more before experiencing collapse.

System is highly secure.

# IEEE14Data (selected- number of  total Tapping Txf available) 3 Capacitor & 100MVAr FVSI:

SIEMENS POWER TECHNOLOGIES INTERNATIONAL

50 BUS POWER SYSTEM SIMULATOR--PSS(R)E Xplore-36.6.0--Python 3.14

INITIATED ON THU, SEP 24 2026  16:40

From bus 7 to 9

Base FVSI       = 0.1208

V_send (pu)     = 0.9648

V_recv (pu)     = 0.9330

P_flow (MW)     = 47.7022

Q_recv (MVAR)   = 25.5549

Q_max (MVAR)    = 43.0356 (Actual network limit)

Q_margin (MVAR) = 17.4807 (Actual margin)

P_loss (MW)     = 0.0000

Q_loss (MVAR)   = 3.7008

From bus 9 to 14

Base FVSI       = 0.0975

V_send (pu)     = 0.9330

V_recv (pu)     = 0.8903

P_flow (MW)     = 16.1511

Q_recv (MVAR)   = 6.4277

Q_max (MVAR)    = 18.9919 (Actual network limit)

Q_margin (MVAR) = 12.5642 (Actual margin)

P_loss (MW)     = 0.4610

Q_loss (MVAR)   = 0.9807

From bus 6 to 13

Base FVSI       = 0.0966

V_send (pu)     = 0.9633

V_recv (pu)     = 0.9223

P_flow (MW)     = 30.4006

Q_recv (MVAR)   = 13.6766

Q_max (MVAR)    = 30.3630 (Actual network limit)

Q_margin (MVAR) = 16.6865 (Actual margin)

P_loss (MW)     = 0.8257

Q_loss (MVAR)   = 1.6261

From bus 6 to 11

Base FVSI       = 0.0749

V_send (pu)     = 0.9633

V_recv (pu)     = 0.9355

P_flow (MW)     = 12.5063

Q_recv (MVAR)   = 7.1109

Q_max (MVAR)    = 21.8062 (Actual network limit)

Q_margin (MVAR) = 14.6953 (Actual margin)

P_loss (MW)     = 0.2187

Q_loss (MVAR)   = 0.4580

From bus 13 to 14

Base FVSI       = 0.0695

V_send (pu)     = 0.9223

V_recv (pu)     = 0.8903

P_flow (MW)     = 9.6325

Q_recv (MVAR)   = 3.4197

Q_max (MVAR)    = 11.8501 (Actual network limit)

Q_margin (MVAR) = 8.4305 (Actual margin)

P_loss (MW)     = 0.2164

Q_loss (MVAR)   = 0.4406

From bus 6 to 12

Base FVSI       = 0.0649

V_send (pu)     = 0.9633

V_recv (pu)     = 0.9325

P_flow (MW)     = 13.3856

Q_recv (MVAR)   = 4.7825

Q_max (MVAR)    = 18.7217 (Actual network limit)

Q_margin (MVAR) = 13.9392 (Actual margin)

P_loss (MW)     = 0.2753

Q_loss (MVAR)   = 0.5730

From bus 11 to 10

Base FVSI       = 0.0358

V_send (pu)     = 0.9355

V_recv (pu)     = 0.9227

P_flow (MW)     = 6.3399

Q_recv (MVAR)   = 3.4483

Q_max (MVAR)    = 12.1209 (Actual network limit)

Q_margin (MVAR) = 8.6726 (Actual margin)

P_loss (MW)     = 0.0502

Q_loss (MVAR)   = 0.1175

From bus 9 to 10

Base FVSI       = 0.0354

V_send (pu)     = 0.9330

V_recv (pu)     = 0.9227

P_flow (MW)     = 8.8778

Q_recv (MVAR)   = 7.9747

Q_max (MVAR)    = 28.5224 (Actual network limit)

Q_margin (MVAR) = 20.5477 (Actual margin)

P_loss (MW)     = 0.0529

Q_loss (MVAR)   = 0.1404

From bus 12 to 13

Base FVSI       = 0.0328

V_send (pu)     = 0.9325

V_recv (pu)     = 0.9223

P_flow (MW)     = 2.8319

Q_recv (MVAR)   = 1.6068

Q_max (MVAR)    = 5.8336 (Actual network limit)

Q_margin (MVAR) = 4.2268 (Actual margin)

P_loss (MW)     = 0.0271

Q_loss (MVAR)   = 0.0246

From bus 4 to 3

Base FVSI       = 0.0212

V_send (pu)     = 0.9524

V_recv (pu)     = 0.9151

P_flow (MW)     = 41.8044

Q_recv (MVAR)   = 2.4313

Q_max (MVAR)    = 23.4923 (Actual network limit)

Q_margin (MVAR) = 21.0610 (Actual margin)

P_loss (MW)     = 1.4013

Q_loss (MVAR)   = 2.4602

RESULT ANALYSIS

Most critical corridor: Bus 7 to 9 (FVSI = 0.1208)

This line can absorb only 17.48 MVAR more before experiencing collapse.

System is highly secure.

# IEEE14Data  9 Capacitor (selected- total PQ available) & 50MVAr FVSI:

SIEMENS POWER TECHNOLOGIES INTERNATIONAL

50 BUS POWER SYSTEM SIMULATOR--PSS(R)E Xplore-36.6.0--Python 3.14

INITIATED ON THU, SEP 24 2026  16:40

From bus 7 to 9

Base FVSI       = 0.1208

V_send (pu)     = 0.9648

V_recv (pu)     = 0.9330

P_flow (MW)     = 47.7022

Q_recv (MVAR)   = 25.5549

Q_max (MVAR)    = 43.0356 (Actual network limit)

Q_margin (MVAR) = 17.4807 (Actual margin)

P_loss (MW)     = 0.0000

Q_loss (MVAR)   = 3.7008

From bus 9 to 14

Base FVSI       = 0.0975

V_send (pu)     = 0.9330

V_recv (pu)     = 0.8903

P_flow (MW)     = 16.1511

Q_recv (MVAR)   = 6.4277

Q_max (MVAR)    = 18.9919 (Actual network limit)

Q_margin (MVAR) = 12.5642 (Actual margin)

P_loss (MW)     = 0.4610

Q_loss (MVAR)   = 0.9807

From bus 6 to 13

Base FVSI       = 0.0966

V_send (pu)     = 0.9633

V_recv (pu)     = 0.9223

P_flow (MW)     = 30.4006

Q_recv (MVAR)   = 13.6766

Q_max (MVAR)    = 30.3630 (Actual network limit)

Q_margin (MVAR) = 16.6865 (Actual margin)

P_loss (MW)     = 0.8257

Q_loss (MVAR)   = 1.6261

From bus 6 to 11

Base FVSI       = 0.0749

V_send (pu)     = 0.9633

V_recv (pu)     = 0.9355

P_flow (MW)     = 12.5063

Q_recv (MVAR)   = 7.1109

Q_max (MVAR)    = 21.8062 (Actual network limit)

Q_margin (MVAR) = 14.6953 (Actual margin)

P_loss (MW)     = 0.2187

Q_loss (MVAR)   = 0.4580

From bus 13 to 14

Base FVSI       = 0.0695

V_send (pu)     = 0.9223

V_recv (pu)     = 0.8903

P_flow (MW)     = 9.6325

Q_recv (MVAR)   = 3.4197

Q_max (MVAR)    = 11.8501 (Actual network limit)

Q_margin (MVAR) = 8.4305 (Actual margin)

P_loss (MW)     = 0.2164

Q_loss (MVAR)   = 0.4406

From bus 6 to 12

Base FVSI       = 0.0649

V_send (pu)     = 0.9633

V_recv (pu)     = 0.9325

P_flow (MW)     = 13.3856

Q_recv (MVAR)   = 4.7825

Q_max (MVAR)    = 18.7217 (Actual network limit)

Q_margin (MVAR) = 13.9392 (Actual margin)

P_loss (MW)     = 0.2753

Q_loss (MVAR)   = 0.5730

From bus 11 to 10

Base FVSI       = 0.0358

V_send (pu)     = 0.9355

V_recv (pu)     = 0.9227

P_flow (MW)     = 6.3399

Q_recv (MVAR)   = 3.4483

Q_max (MVAR)    = 12.1209 (Actual network limit)

Q_margin (MVAR) = 8.6726 (Actual margin)

P_loss (MW)     = 0.0502

Q_loss (MVAR)   = 0.1175

From bus 9 to 10

Base FVSI       = 0.0354

V_send (pu)     = 0.9330

V_recv (pu)     = 0.9227

P_flow (MW)     = 8.8778

Q_recv (MVAR)   = 7.9747

Q_max (MVAR)    = 28.5224 (Actual network limit)

Q_margin (MVAR) = 20.5477 (Actual margin)

P_loss (MW)     = 0.0529

Q_loss (MVAR)   = 0.1404

From bus 12 to 13

Base FVSI       = 0.0328

V_send (pu)     = 0.9325

V_recv (pu)     = 0.9223

P_flow (MW)     = 2.8319

Q_recv (MVAR)   = 1.6068

Q_max (MVAR)    = 5.8336 (Actual network limit)

Q_margin (MVAR) = 4.2268 (Actual margin)

P_loss (MW)     = 0.0271

Q_loss (MVAR)   = 0.0246

From bus 4 to 3

Base FVSI       = 0.0212

V_send (pu)     = 0.9524

V_recv (pu)     = 0.9151

P_flow (MW)     = 41.8044

Q_recv (MVAR)   = 2.4313

Q_max (MVAR)    = 23.4923 (Actual network limit)

Q_margin (MVAR) = 21.0610 (Actual margin)

P_loss (MW)     = 1.4013

Q_loss (MVAR)   = 2.4602

RESULT ANALYSIS

Most critical corridor: Bus 7 to 9 (FVSI = 0.1208)

This line can absorb only 17.48 MVAR more before experiencing collapse.

System is highly secure.

PS D:\EEE 305 PSSE Project> & C:\Users\kawsa\AppData\Local\Microsoft\WindowsApps\python3.13.exe "d:/EEE 305 PSSE Project/Python Codes/FVSI-Collapse Analysis.py"

PSS(R)E Xplore Version 36

Copyright (c) 1976-2026

Siemens Industry, Inc.,

Power Technologies International                            (PTI)

This program is a confidential  unpublished  work  created  and  first

licensed in 1976.  It is a trade secret which is the property of  PTI.

All use,  disclosure,  and/or reproduction not specifically authorized

by  PTI  is prohibited.   This  program is protected  under  copyright

laws  of  non-U.S.  countries  and  by  application  of  international

treaties.  All  Rights  Reserved  Under  The  Copyright  Laws.

SIEMENS POWER TECHNOLOGIES INTERNATIONAL

50 BUS POWER SYSTEM SIMULATOR--PSS(R)E Xplore-36.6.0--Python 3.14

INITIATED ON THU, SEP 24 2026  16:41

From bus 7 to 9

Base FVSI       = 0.1208

V_send (pu)     = 0.9648

V_recv (pu)     = 0.9330

P_flow (MW)     = 47.7022

Q_recv (MVAR)   = 25.5549

Q_max (MVAR)    = 43.0356 (Actual network limit)

Q_margin (MVAR) = 17.4807 (Actual margin)

P_loss (MW)     = 0.0000

Q_loss (MVAR)   = 3.7008

From bus 9 to 14

Base FVSI       = 0.0975

V_send (pu)     = 0.9330

V_recv (pu)     = 0.8903

P_flow (MW)     = 16.1511

Q_recv (MVAR)   = 6.4277

Q_max (MVAR)    = 18.9919 (Actual network limit)

Q_margin (MVAR) = 12.5642 (Actual margin)

P_loss (MW)     = 0.4610

Q_loss (MVAR)   = 0.9807

From bus 6 to 13

Base FVSI       = 0.0966

V_send (pu)     = 0.9633

V_recv (pu)     = 0.9223

P_flow (MW)     = 30.4006

Q_recv (MVAR)   = 13.6766

Q_max (MVAR)    = 30.3630 (Actual network limit)

Q_margin (MVAR) = 16.6865 (Actual margin)

P_loss (MW)     = 0.8257

Q_loss (MVAR)   = 1.6261

From bus 6 to 11

Base FVSI       = 0.0749

V_send (pu)     = 0.9633

V_recv (pu)     = 0.9355

P_flow (MW)     = 12.5063

Q_recv (MVAR)   = 7.1109

Q_max (MVAR)    = 21.8062 (Actual network limit)

Q_margin (MVAR) = 14.6953 (Actual margin)

P_loss (MW)     = 0.2187

Q_loss (MVAR)   = 0.4580

From bus 13 to 14

Base FVSI       = 0.0695

V_send (pu)     = 0.9223

V_recv (pu)     = 0.8903

P_flow (MW)     = 9.6325

Q_recv (MVAR)   = 3.4197

Q_max (MVAR)    = 11.8501 (Actual network limit)

Q_margin (MVAR) = 8.4305 (Actual margin)

P_loss (MW)     = 0.2164

Q_loss (MVAR)   = 0.4406

From bus 6 to 12

Base FVSI       = 0.0649

V_send (pu)     = 0.9633

V_recv (pu)     = 0.9325

P_flow (MW)     = 13.3856

Q_recv (MVAR)   = 4.7825

Q_max (MVAR)    = 18.7217 (Actual network limit)

Q_margin (MVAR) = 13.9392 (Actual margin)

P_loss (MW)     = 0.2753

Q_loss (MVAR)   = 0.5730

From bus 11 to 10

Base FVSI       = 0.0358

V_send (pu)     = 0.9355

V_recv (pu)     = 0.9227

P_flow (MW)     = 6.3399

Q_recv (MVAR)   = 3.4483

Q_max (MVAR)    = 12.1209 (Actual network limit)

Q_margin (MVAR) = 8.6726 (Actual margin)

P_loss (MW)     = 0.0502

Q_loss (MVAR)   = 0.1175

From bus 9 to 10

Base FVSI       = 0.0354

V_send (pu)     = 0.9330

V_recv (pu)     = 0.9227

P_flow (MW)     = 8.8778

Q_recv (MVAR)   = 7.9747

Q_max (MVAR)    = 28.5224 (Actual network limit)

Q_margin (MVAR) = 20.5477 (Actual margin)

P_loss (MW)     = 0.0529

Q_loss (MVAR)   = 0.1404

From bus 12 to 13

Base FVSI       = 0.0328

V_send (pu)     = 0.9325

V_recv (pu)     = 0.9223

P_flow (MW)     = 2.8319

Q_recv (MVAR)   = 1.6068

Q_max (MVAR)    = 5.8336 (Actual network limit)

Q_margin (MVAR) = 4.2268 (Actual margin)

P_loss (MW)     = 0.0271

Q_loss (MVAR)   = 0.0246

From bus 4 to 3

Base FVSI       = 0.0212

V_send (pu)     = 0.9524

V_recv (pu)     = 0.9151

P_flow (MW)     = 41.8044

Q_recv (MVAR)   = 2.4313

Q_max (MVAR)    = 23.4923 (Actual network limit)

Q_margin (MVAR) = 21.0610 (Actual margin)

P_loss (MW)     = 1.4013

Q_loss (MVAR)   = 2.4602

RESULT ANALYSIS

Most critical corridor: Bus 7 to 9 (FVSI = 0.1208)

This line can absorb only 17.48 MVAR more before experiencing collapse.

System is highly secure.